| FIELD SERVICE REPORT |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| TriStar Engineers & Services D-514, Kalindi Vihar, Agra M#9045254014, 4016, 4012, 9557528916 Email- support@tristarengineer.com, tses@gmail.com |  |  |  |  |  |  | CRM ID: CRM-10233213 |  |  |
|  |  |  |  |  |  |  | Call | Date | Time |
|  |  |  |  |  |  |  | Received On | 2025-01-10 |  |
|  |  |  |  |  |  |  | Attended On | 2025-01-12 |  |
|  |  |  |  |  |  |  | Cognised On | 2025-01-13 |  |
| Customer Name & Address: ABC Industries, Plot 45, Industrial Area, Delhi |  |  |  |  |  | Contact Person | Rohit Kumar |  |  |
|  |  |  |  |  |  | Contact Number | 9876543210 |  |  |
|  |  |  |  |  |  | Email ID | support@abcindustries.com |  |  |
|  |  |  |  |  |  | Website | https://abcindustries.com |  |  |
| Nature of Complaints: UPS not switching to backup |  |  |  |  |  |  |  |  |  |
| Serial Number: undefined |  |  |  | Model: SmartX-10KVA |  |  | Capic: 10 KVA |  |  |
| Product: UPS System |  |  |  |  |  |  |  |  |  |
| Configuration: Online UPS with external batteries |  |  |  |  |  |  |  |  |  |
| Battery Details: SMF 12V 9AH x 16 |  |  |  |  |  |  |  |  |  |
| Type of Faults | Power supply fault |  |  |  |  |  |  |  |  |
| Complaint Details |  | Customer reported UPS not switching to battery mode. |  |  |  |  |  |  |  |
| Diagnosis / Observation: |  | Found faulty charging card. |  |  |  |  |  |  |  |
| Collective Action / Remarks |  | Replaced charging card and tested successfully. |  |  |  |  |  |  |  |
|  | I/P Volts |  |  | DC Output |  |  | Battery |  |  |
| Important | RN | YN | BN | VOLT | AMP |  | VOLT | AMP |  |
| Parameters | 230 | 231 | 229 | 108 | 12 |  | 13.4 | 7.5 |  |
|  | O/P Volts |  |  | O/P AMPS |  |  | I/P Earth Volt |  |  |
| Important | RN | YN | BN | R | Y | B | PE | NE |  |
| Parameters | 230 | 232 | 228 | 3.2 | 3.4 | 3.1 | 0.5 | 0.8 |  |
| Components Replaced if any |  |  |  |  |  |  |  |  |  |
| S. No. | Description |  |  |  |  |  |  | Quantity |  |
| 1 | Charging card |  |  |  |  |  |  | 48 |  |
| 2 | net cart |  |  |  |  |  |  | 9 |  |
| 3 |  |  |  |  |  |  |  |  |  |
| 4 |  |  |  |  |  |  |  |  |  |
| 5 |  |  |  |  |  |  |  |  |  |
| 6 |  |  |  |  |  |  |  |  |  |
| Components Need to Replace |  |  |  |  |  |  |  |  |  |
| S. No. | Description |  |  |  |  |  |  | Quantity |  |
| 1 | Charging card |  |  |  |  |  |  | 48 |  |
| 2 | net cart |  |  |  |  |  |  | 9 |  |
| 3 |  |  |  |  |  |  |  |  |  |
| 4 |  |  |  |  |  |  |  |  |  |
| 5 |  |  |  |  |  |  |  |  |  |
| 6 |  |  |  |  |  |  |  |  |  |
| 7 |  |  |  |  |  |  |  |  |  |
| Technical Suggestion if any :- Regular maintenance recommended. |  |  |  |  |  |  |  |  |  |
| Customer Comments if any |  | UPS running fine after repair. |  |  |  |  |  |  |  |
| Reported Complaints have been Rectified, Servicing Done to Our Satisfaction. We agree to pay your Charges for the same if applicable |  |  |  |  |  |  |  |  |  |
| Customer Sign & Seal jdosadsa Contact Name: Arjun Mehta Designation: Maintenance Manager Contact Number: 9988776655 |  |  | Equipment is OK |  | YES | Connected Load:- 8 KVA |  |  |  |
|  |  |  | Equipment is Not OK |  | NO |  |  |  |  |
|  |  |  | Call Carried Over |  | YES |  |  |  |  |
|  |  |  | Call Chargeable |  | NO |  |  |  |  |
| Customer Care Number : 9045254014 |  |  |  | Email : support@tristarengineer.com |  |  | Tristarengineer.com |  |  |